## Slide 1: An Integrated Approach to Operational Efficiency & Reliability
Achieving operational excellence at every step of the data center life cycle, from design through sustained operations.
James Bartone
Global Technical Committee Member
Schneider Electric
Marina Thiry
Operations Work Group Chair
ABB
Notes: Good afternoon everyone. My name is James Bartone. I work for Schneider Electric IT as a Program Manager in the Data Center Software Solutions group. I also am the Vice Chair of the TGG NAM Technical Committee.
My co-presenter today is Marina Thiry who is the Director of Strategic Marketing for the Control Technologies group in the Process Automation division at ABB. Marina is also the TGG Operations WG Chair and holds a leadership position in the DCIM IG.
Today Marina & I are going to discuss the data center lifecycle with a focus on systems integration for increasing efficiency and reliability.
My portion of the talk will focus on a ‘how-to’ approach for achieving integration during Design--Commissioning based on recommendations presented in TGG WP-52 entitled ‘An Integrated Approach to Operational Efficiency & Reliability’.
Marina will pick up the conversation to discuss how DCIM can serve as a powerful tool for monitoring and maintaining efficiency and reliability, as well as managing change and planning for the future during the Sustained Operations period of the data center lifecycle.

## Slide 2: Facility Operations Challenge:
Operational Documentation
    Non-Existent
    Inadequate
    Disorganized/Scattered
    Equipment-specific only
Sequence of Operations
    Systems info non-existent or HVAC controls only
    Systems interoperability information - None
    No ‘holistic’ picture (addressing entire data center)
Notes: FACILITY OPERATIONS CHALLENGE
I came to Schneider Electric via Lee Technologies which is now SE Mission Critical Services. MCS operates and maintains data centers for large customers all over the world using written procedures that are tailored for each facility that we manage. It seems that whenever we mobilize to assume Facility Operations responsibility for a new account, especially in legacy data centers, we encounter the same challenges --unreliable operational documentation that must serve as the basis of our written processes and procedures, and very little information about systems interoperability.
Operational Documentation is either
  Non-Existent, Inadequate, or scattered around the DC
  Info that is available is typically Equipment-specific only
Systems Information such as Sequence of Operations
  Typically for HVAC controls only
  No ‘holistic’ picture (addressing entire data center
The results of poor Operational documentation include:
Owner’s Project Requirements - not met
Performance & Efficiency - not optimized
Operational Costs - rise
Reliability – suffers and ultimately
System Failure Risk - is increased
These impacts are experienced over the entire Sustained Operations Period which is longest & most costly data center life cycle phase.

## Slide 3: Change the Industry
  Universal DC industry problem must be addressed:
    Inadequate or inaccurate Facility Operations Documentation results in non-optimized data center performance due to uncertainty or lack of information
  Process issue
    Lack of operational focus & required documentation during design and construction
    Incompatible data collection formats utilized during design, construction, and commissioning
    Inadequately specified requirements for operational documents ‘turnover’ at project completion
    Non-integrated change management system
Notes: We identified the key challenges to better OpDoc as:
- Lack of Ops focus during design
Loss of field generated data during Construction
Changes in the work
To address the documentation problem, we determined that we had to ‘change the industry’ by developing and implementing a process for delivering efficient, reliable data centers to our FO teams at ‘Go Live”; and maintain a high-reliability status by effectively managing change throughout the data center lifecycle.

## Slide 4: Recommendation
TGG White Paper #52 - An Integrated Approach to Operational Efficiency & Reliability provides prescriptive measures for better data collection, integration, and change management practices throughout the entire facility lifecycle
  Lists and defines required operational documents for turnover to Facility Operations team
  Recommends employing a commissioning consultant from schematic design phase through ‘Go Live’ turnover
  Presents a formulated approach for producing a holistic facility sequence of operations manual that is delivered to the Facility Operations team at turnover
  Defines and outlines Sequence of Operations format
Notes: The culmination of our work can be found in WP 52 which:
Provides listing of key OpDocs
Recommends including the Cx Consultant early in Design
Defines SOO Manual & provides the “how-to” to achieve it
Process involved:
First identifying and compiling a list of documents required to fully understand the facility, including the equipment line-up, operational sequences, and inter-system interoperability.
We then determined the point of time in the DC lifecycle when these documents were developed and could be collected.
We also realized that the Commissioning Consultant should be a key member of the Design team and prepare the Cx Plan prior to construction.
The following chart illustrates some of our findings.

## Slide 5: Facility Life Cycle & Operational Docs
Notes: FACILITY LIFE CYCLE & OPERATIONAL DOCS
Subtitle is: SOO & the Data Center Lifecycle (today’s focus)
- The multicolored horizontal arrow chronologically lists the phases of the DC life cycle.
- The color-corresponding boxes below each arrow contain the names of the required OpDocs developed during each phase.
- The black arrows between boxes illustrate the development of the facility-wide operational sequences which will become the facility Operations & Maintenance manual during Turnover.
The next few slides provide a brief overview of operational Integration considerations during the Design, Construction, and Commissioning phases of the data center lifecycle. Because of time constraints, I won’t drill too deeply into Design or any of the lifecycle phases for that matter. However, WP-52 offers in depth look at the team interactions, processes, and deliverables of each lifecycle phase as they relate to Operations integration. I encourage you download it from TGG website for the full story. Today I will only emphasize a few key points made in the paper.

## Slide 6: Design Phase
  Schematic Design (SD)
    Budget & schedule established
    Systems to be commissioned identified
  Design Development (DD)
    Building architecture and floor plans ‘locked’
    Primary critical infrastructure systems selected
  Construction Documents (CD)
    Construction drawings & specifications
    Operational sequences identified
    Commissioning plan completed
Notes: Let’s start with the DESIGN PHASE:
A summary of the formal design process is presented here with key Operational milestones of each.
Today’s programming and design process is fairly standardized; however, it lacks an Operational focus. To counter this deficiency, we recommend that the CxA join the design team early in the design process and stay engaged through project turn-over. The Cx Consultant’s contributions are applicable to the following deliverables listed on the slide:
SD- Systems to be commissioned identified early
DD- Primary critical infrastructure systems & monitoring & control systems are selected
CD- Ops sequences identified & Cx plan completed

## Slide 7: Commissioning (Cx) Plan
Commissioning Consultant (CxA) prepares:
  Under jurisdiction of Design Integrator
  Draft to be completed by 60% CD review
  Separate Cx Specification section required
Roadmap for all critical infrastructure testing
  Narrative descriptions/scripts (step-by-step instructions)
  Graphical depictions (order-based, time-sequenced)
Operations Sequences are defined
  Systems to be commissioned identified
  Equipment functionality and interoperability tested
Notes: COMMISSIONING (CX) PLAN
The Cx consultant, works under the Lead Designer, and prepares the Cx plan consisting of testing scripts (step-by-step instructions) to assure as-designed performance of all equipment, each individual system, and all systems working together as a whole (integrated fashion).
Although Commissioning of some sort is currently universal, the Cx consultant is typically injected into most projects at 60% construction completion. We recommend that their involvement begin in late schematics or early Design Development. To drive home the importance of the this point, I’d like to read a quote from the National institute of Building Science – US Green Building Council’s - Whole Building Design Guide (LEED):
“It is important to start the commissioning process early and to bring the commissioning agent (CxA) on board during or before schematic design. This early involvement is critical for the timely and useful development of the Owner's Project Requirements (OPR), the subsequent design team Basis of Design (BOD) and the beginning of the Operations and Maintenance (O&M) manual. If these tasks are left until later in the process and "reverse engineered" to match the design, their usefulness as catalysts for dialog and quality tracking tools is lost.”
WP-52 also recommend a separate Commissioning Specification section be included in the Project Manual to clearly define commissioning requirements prior to bidding and contracting.

## Slide 8: Construction Phase Issues
Substitutions and change orders
  Owner accepted for cost savings or other reasons
  Unforeseen conditions, errors, omissions, etc.
  Must be vetted against BOD and Cx Plan
  All related documents must be revised & distributed
Operational data supplied by contractor
  Equipment info: ID, serial no., location, installation date
  Start-up data, statistics & performance information
  No standard data format (incompatible software tools)
  Information lost or not integrated into project record
Notes: OK, let’s jump to Construction:
The two key areas of concern during Construction are Field-generated Data Collection & Changes in the work.
The term “Change Order” is synonymous with Construction. Change Orders aren’t necessarily bad. The most important aspect of Change orders from an operations perspective:
They must be vetted against BOD and Cx Plan
approved by the project sponsor
all affected documents must be revised to reflect the changed condition, and
distributed to all.
Field Data Loss:
Contractors develop and collect a lot of data during the course of Construction. However, because there is no standard format for data collection, or software compatibility standards; vital equipment information, although submitted by Contractors, often doesn’t make it into the project record.
WP-52 goes in depth discussing tools for overcoming this challenge such as:
COBie (Construction Operations Building Information Exchange) developed by the USAEC
BIM (Building Information Models) pioneered by Stanford University --- but due to timing, we won’t cover those now.

## Slide 9: Commissioning Process
Five Commissioning Levels
  1: Document review
    Cx Script preparation
  2: Post construction inspections
    Insures conformance to plans and specifications
  3: Start-up equipment
    By contractor using manufacturer’s checklists
  4: Functionally test equipment
    By contractor using CxA scripts
  5: Integrated Systems Test
    Includes Facilities Ops team (training)
Notes: Because Cx is sometimes defined differently, here’s how WP-52 presents the Five Cx Stages of Cx
  1: Document review - Cx Scripts are prepared by the CxA
  2: Post construction field inspections – Insures the installation conforms to Plans and Specs.
  3: Start-up equipment - By Contractor using manufacturer’s checklists simply to confirm that they are working
  4: Functionally test equipment - Each individual mode of operation of each piece of equipment tested by the Contractor using CxA scripts
  5: Integrated Systems Test – Simultaneous tests of all systems to assure holistic or integrated performance (Big daddy)
  WP-52 recommends that Facilities Ops team participate in IST (no risk training exercise during actual failure scenarios)

## Slide 10: Cx Report and its Uses
Cx report contents
  Test scripts (step-by-step instructions)
  Test results and data
  Component error log
  Trending reports
  Basis of DCIM assumptions
Cx report uses
  Benchmarking future data center performance
  Predicting results of unplanned events
  Assessing risk prior to making changes
  Basis of SOO Manual
Notes: Following a successful IST, the CxA publishes the Commissioning report that:
includes all data gathered during Commissioning, and
serves as the initial benchmark for DC performance,
fail-over prediction, and risk assessment.
CX Report will be incorporated into the SOO manual which is described during the next few slides.

## Slide 11: Facility Life Cycle & Operational Docs
Notes: FACILITY LIFE CYCLE & OPERATIONAL DOCS
Now that we’ve touched on some Operational considerations during Design, Construction & Commissioning, Let’s trace the development of the SOO and Operations & Maintenance Manual by following the Black lines that link key documents.
During PP & Design: The OPR Building ProgramBOD which is the foundation for the IFC DWGS/Specs/Cx Plan .
Construction: Submittals, Shop Drawings, and Equipment lists and other data are produced by the Contractor and collected. Additionally changes are documented & incorporated.
Commissioning & Turnover follows. The Cx Report is released. It provides an accurate picture of the facilities equipment, systems, sequences, and interoperability. This accumulated information is used to produced the Operations & Maintenance Manual by the FO team during Turn-over.
We’ll discuss Turn-over & Sustained Operations shortly, but first let’s drill-down into the SOO Manual.

## Slide 12: Sequence of Operations Manual
Hierarchy
  Facility responding to its ambient environment
  Systems interacting with each other (interoperability)
  System internal sequencing (intra-operability)
  Equipment level detail
Components
  System Outline – standard format
  Narratives – ‘drill-down’ detail
  Diagrams – logic-based flow charts
  Design phase operational sequences and Cx findings
Notes: SEQUENCE OF OPERATIONS MANUAL
The SOO Manual consists of two distinct parts:
detailed written Narratives, and
supporting graphic Diagrams
It graphically illustrates and narratively describes:
- DC process flows and information
needed to perform day-to-day facility operations,
and to respond to unscheduled events.
Format: ‘drill-down’ from ‘whole’ to component ‘parts’:
  Entire Facility sited in its unique environment
  Inter-Systems relationships within the facility
  Individual System sequences
  Equipment level detail
Should include
Resource information about the data center, & its hardware, and software.
Process information, including sequencing during normal, by-pass, failure, and test modes, for safe, proactive operation and emergency response.
The next 3 slides provide examples of the outline, narratives, and graphics recommended for the SOO Manual.

## Slide 13: SOO Systems Outline
Overview
  Site and Building Parameters
  Power Distribution System
  Cooling Systems
  Mechanical Systems
  Monitoring & Control Systems
  Data Infrastructure
Power Systems
  Utility Power
  No-Break Power/Uninterruptable Power Systems
  Short-Break Power/Back-Up Systems
  House Power
Cooling Systems
  HVAC System
  Humidification & Dehumidification Systems
  Data Center Air Circulation
  Outside Air & Filtration
  Remainder of Cooling
  Ventilation
Notes: Here is the SOO Outline:
As you can see, It begins with a general Overview of its Main Critical Infrastructure systems such as (Site & Building, Power, etc. through Data Infrastructure).
Each major system is then listed individually with a breakdown of their subsystems. The subsystems are described in great detail in the SOO manual using both descriptive narratives and flow diagrams.
Let’s take a look at a section of a sample Narrative:

## Slide 14: SOO Systems Outline Cont’d
Infrastructure Management Systems (DCIM)
  Electrical Power Management System
  Building Management System
  Aspirating Smoke Detection System
  Fire Alarm
  Fuel System
  Leak Detection
  Access Control and Security Systems
Mechanical Systems
  Fuel System Pumping and Piping
  Storage Tanks
  Spill Containment
  Fire Suppression System
  Industrial Water System Pumping and Piping
  Other Utility Piping
Data Infrastructure Systems
  Distribution
  Media Types
  Management
Notes: Here is the SOO Outline:
As you can see, It begins with a general Overview of its Main Critical Infrastructure systems such as (Site & Building, Power, etc. through Data Infrastructure).
Each major system is then listed individually with a breakdown of their subsystems. The subsystems are described in great detail in the SOO manual using both descriptive narratives and flow diagrams.
Let’s take a look at a section of a sample Narrative:

## Slide 15: Narrative Excerpt
    5. UNINTERUPTIBLE POWER SYSTEMS
      UPS-1
        Normal Operation:
          Supplies critical load to CD11
        Maintenance Operation:
          Place system into internal bypass. Use MBB-1 to bypass UPS. Open the module batteries disconnect (MBD) circuit breaker by simultaneously pressing the Battery Trip and Control Enable pads. Manually open the UPS input circuit breaker by moving the handle to the OFF position. UPS is isolated for work.
        Fault Operation:
          Upon a loss of input power the batteries will discharge to maintain required load.
          If the unit is unable to maintain required voltage, the system will go to internal bypass.
      UPS-2
Notes: Here is an example extracted from a Power subsystem narrative of an actual DC in the US Northwest.
UPS-1 operation is described in Normal, By-pass/maintenance, and in fault/failure modes.
Energy flows during Automatic operations, as well as detailed instructions for manual operation, are described for each piece of equipment in the line-up..
Ideally, every narrative will have a corresponding graphic.

## Slide 16: Flow Chart Diagram Example
Notes: I apologize for this slide, but I think it gets the idea across.
The point is that each System & Sub-system should be charted as a process/decision diagram that illustrates process flows under various conditions and operational states.

## Slide 17: Facility Ops Integration Goals
Optimally performing data center
  Collaborative Systems
  Clearly Defined Operating Parameters
Clear documentation
  Processes
  Procedures
Change management system
  Consistent format
  Version Control
All of the above at “Go Live!”
Notes: TGG WP-52 “An Integrated Approach to Operational Efficiency and Reliability” presents a practical ‘how-to approach’ for instilling an Operations focus during design, construction & commissioning so the FO team has the information they need to operate and maintain:
Optimally Performing Data Center
  Collaborative Systems
  Clearly Defined Operating Parameters
Clear Documentation
  Processes
  Procedures
Change Management System
  Consistent format
  Version Control
All of the above at “Go Live!”

## Slide 18: Facility Life Cycle & Operational Docs
Notes: Finally, before Marina comes up to talk about how DCIM fits into this picture, let’s quickly complete our overview of the DC lifecycle.
Turnover & Transition follows Cx – it is the shortest phase of Facility Life Cycle (45-60 days). As short as it is, during this time for the FO team must:
- Collect Operational Documents
- Author Operating Procedures & establish Technical library
- Train on all systems and equipment
Sustained Operations follows, its the longest phase of Facility Life Cycle (years). It is characterized by constant change (equipment added or removed) due to Customer needs, Changing business conditions, Technological innovation & Legacy systems upgrades
Change must be managed using a Standardized Change Process involving
Review of ‘downstream’ & ‘inter-system’ impacts
Documenting approved changes (version control)
Updating related Operational documents including
Sequence of Operations &
Supporting docs (such as as-built, O&Ms, procedures)
With that said, I’m going to pass the ball to Marina now. She will be discussing how DCIM can be a powerful tool for maintaining efficiency, managing change, and planning for the future during the Sustained Operations phase of the data center lifecycle.

## Slide 19: The Expanding Role of DCIM
The latest definitions and models of a DCIM system
How DCIM helps with integrating data center operations
Examples of how DCIM is being used to better manage cost, capacity and control throughout the data center life cycle
Notes: Thank you, James… Hi, I’m Marina Thiry with ABB… When James invited me co-present on this topic, he asked that I address the expanding role of DCIM in the data center life cycle. So, I’ll start by introducing the latest definitions and models of a DCIM system, and then explain how it can help with integrating operations. And, I’ll close by providing a few examples of how DCIM is being used to better manage cost, capacity and control throughout the data center life cycle.
If you work in a data center, whether you’re working on the IT side or the facility side, then it’s a safe bet that you are an excellent problem-solver… Your attention to detail, your recognition of patterns and outliers, and your affinity to solve problems are the basis for your success with data center operations… That said, I think you’ll appreciate the analogy that speaks to both problem-solving capabilities and a DCIM system.

## Slide 20: Q. What is the single most significant factor that has impacted the evolution of human brains and DCIM systems?
A. Environmental instability. Constant change.
Notes: Let’s tee up the analogy with this question: What is the single most significant factor that has impacted the evolution of the human brain and the DCIM system? … Do you know the answer?
<click> The answer is environmental instability. Constant change.
As we shall see, a DCIM system is indeed like the brain of a data center.

## Slide 21: An Integrated Approach
Alerting network
Data collection and normalization
Your Brain
Your DCIM
Orienting network
Executive network
Visibility and decision support
Action and/or automation
Notes: Some of you may be familiar with the work of Dr. John Medina. He’s a developmental molecular biologist who studies how the mind reacts and organizes information. In his New York Times best seller, Brain Rules, he explains that “Environmental instability has led to the extremely flexible way our brains are wired to solve problems.” He references the Trinity Model which identifies three separate but fully integrated systems in the brain…
<click> The first system, called the Alerting Network, monitors the sensory environment for any unusual activities. If the system detects something unusual, then it sounds an alarm in the brain and transforms our alert state into specific attention, thereby orienting ourselves to that stimulus…<click> This is similar to a DCIM system, which monitors and collects all kinds of data types from all kinds of components, equipment and systems, including energy consumption and environmental data. The system then normalizes and processes that data for assessment. It will also send an alarm if it detects anything unusual.
<click> Next, the Alerting Network triggers the Orienting Network. The purpose of this second system is to gain more information about the stimulus, allowing us to decide what to do… <click> Sounds like a DCIM system right? …A DCIM system will analyze and present information in the form of dashboards and reports, thereby providing visibility and decision support. For example, it can show you in real-time when, where and at what rate energy is being consumed. It can show you, with a single click on the dashboard, contextually relevant information to what is being shown, such as prescriptive instructions, like the sequence of operations or user manuals.
<click> The third system, called the Executive Network, controls behaviors, such as setting priorities, planning on the fly, or shifting attention… <click> Here, a DCIM system enables you to take action or even dispatch automation.
A DCIM system is to the data center what your brain is to you! Various systems working together to collect and assess all kinds of data types so you can better manage your data center. A good DCIM system provides the contextualized decision support and controls to expedite the right behavior from the operations team. The fundamental capabilities are: (1) data collection and normalization, (2) visibility and decision support, and, (3) enablement to perform well—directly or through automation.

## Slide 22: Constant Change
Changing compute workloads that impact HVAC systems
Increasing energy costs that squeeze operating budgets and curtail resources
Contaminants that clog and corrode our systems
New technologies that require integration—without which we can’t continue to evolve
Notes: Furthering this analogy, consider that as our data center operations grow larger and more capable, it needs to overcome environmental instability to sustain. Environmental instability comes in many forms--and many of these changes are not immediately visible or obvious, such as:
changing compute workloads that impact HVAC systems,
increasing energy costs that squeeze operating budgets and curtail resources,
contaminants that clog and corrode our systems, and
new technologies that require integration—without which we can’t continue to evolve.
As the data center evolves—whether it’s expanding or consolidating or keeping in step with business demands—there is far more data than we can see and process in our own brains to keep the data center running without a hitch. And the ever-increasing reliance of business on data centers is irrefutable. It’s far too costly simply to “hope” that we have the right information to avoid an unscheduled outage. In short, this is why we are relying more on our DCIM system.
Next, let’s take a look at what exactly a DCIM system is and how its usage is expanding in the data center.

## Slide 23: DCIM Definitions and Models
451 Research (circa 2014)
Data Center Infrastructure Management (DCIM)
Datacenter Service Optimization (DCSO)
Data Center Business Planning
Data Center Service-Based Costing
Data Center Service Management
Data Center Energy Management
Cooling Optimization
Data Center Asset Capacity Mgmt
Data Center Monitoring
Core DCIM Platform
Gartner Research (circa 2011)
enables more AGILITY
Notes: The term DCIM was coined a few years ago. Leading industry analysts helped define what was material to a DCIM system, and today their definitions haven’t changed much—but the their models have evolved as more optimization services are used to help plan and manage constant change and to help automate processes in the data center.
For example, let’s take a quick look at definitions and models from Gartner Research and 451 Research. In short:
Gartner’s definition is, “…tools that optimize data centers by monitoring and managing IT and facility resources and energy consumption."
451’s definition is, “a system that collects and manages information about a data center’s assets, resource use and operational status.”
Both research firms go on to explain that this information is processed, integrated, analyzed and applied in ways that help managers meet business and service-oriented goals while continually optimizing their data center’s performance.
The definitions are nearly identical, but the models look very different. Gartner’s model, introduced around 2011, holds up very well. It includes a controls component and resembles what we see in the process automation industry. 451 recently introduced this model. It resembles a software stack. <click> Indeed, they are emphasizing SaaS capabilities on top of the DCIM platform.
What is different today are the services that work with a DCIM system for planning and optimization—including automation—such as business planning, service-based costing, service management and energy management.
These services enable a more agile data center. A DCIM system is no longer “just” about compute, network and storage capacity supported by the physical infrastructure. Now, there is a growing business need for data center operators to account for factors independent of the facility. For example, insight into highly virtualized environments, as well as the economics and latency of data services.

## Slide 24: Why Use DCIM to Integrate Ops?
Power Management
Energy Management
Facility Management
Maintenance Management
Troubleshooting, Root Cause Analysis & Alarm Management
Resource Forecasting & Energy Planning
Asset & Capacity Planning
Control and Automation
Remote Monitoring
Data Center Evolution
Notes: Another HUGE reason for DCIM’s expanding role in the data center is that it helps integrate operations… Let’s take a look at this illustration of a data center landscape to see why.
Here, we see the power chain—from distributed energy sources to servers in the racks. Plus we see the cooling infrastructure and even a NOC. Also, the top 10 capabilities necessary to manage a data center are labeled here. Many of us in this room have specific expertise related to one or more of these capabilities. Each area of expertise has its own tools and technologies, for example:
<click> Your BMS may use BACnet.
<click> Your PMS may use Modbus, as well as hardwired I/O.
<click> Your EMS may use custom protocols, like ION.
<click> And, your IT systems may use SNMP, IPMI, ILOM, and so on.
The specialization required to run a mission critical facility can frequently contribute to chaos because of the lack of shared visibility and integration. Using a DCIM system helps take out the chaos from managing a data center because, fundamentally, it is the platform that enables you to have a truly holistic view of your data center operations. A good DCIM system is purpose-built to collect and normalize data from all types of communication protocols. A holistic view means the data set is complete: In theory, there are no gaps from which to arrive at faulty conclusions because of missing data..
What I’ve just explained is not novel, but it does require ‘heavy lifting’ in terms of software development. It’s worthwhile to investigate how effectively this process is managed, including security considerations. Many DCIM system providers claim to do this, but how well its accomplished varies significantly.
Equally important: A DCIM system is the platform from which to integrate NEW technologies that will help your data center evolve and achieve even greater operational benefits down the road. It’s one component of a comprehensive data center management strategy that improves reliability and efficiency today and on the horizon.

## Slide 25: Managing the [3 Cs]
How do you better manage IT and facility capacity to lower energy consumption and avoid penalties from overages?
When UPS goes on battery, what other devices are impacted? What other parts of the business are at risk?
How do you evolve data center operations to ‘the next level’ without compromising reliability and becoming inefficient or unsustainable?
Cost
Capacity
Control
Notes: The expanding role of DCIM is due in large part because it provides the capabilities to manage constant change throughout the data center life cycle. Many of these changes impact the 3 Cs in your data center <click> : cost, capacity and control.
<click > Here are some of the typical challenges that our customers and prospects have shared with us. You may have encountered these challenges yourself... <read slide>
Now let’s jump in to a few real-world examples. In the following 3 ‘Example’ slides, you won’t be able to see the details. That’s OK. What’s important is to have a general understanding of what is being shown. In each example, I’ll describe the data center team’s challenge, their approach to overcoming the challenge, factors they identified as critical to success, and the results.

## Slide 26: Example #1: Cost
Power chain
Cooling chain
Notes: Example #1 addresses cost—and it can be applied from the design phase through sustained operations. It’s based on the experiences of a colo and managed hosting provider.
This slide shows two dashboards from a DCIM system:
The left dashboard shows a high level overview of the power chain from the input feed to the rack: the generator, the switchgear, the branch circuits, the UPSs, etc. You can drill down on any component to see more detail. For example, by clicking on a component you can see context-sensitive documentation, such as warranties and procedures.
The right dashboard shows a high level overview of the cooling chain. This screen shows the Glycol loop for this data center, including a summary displaying the status of each unit, plus its leak and valve status. Again, you can drill down and see details. For example, if a ball-bearing in a pump degrades and the system becomes less efficient, you’ll quickly see the issue and can have it remedied before it turns into an expensive problem.
The value of seeing a high level overview of your data center infrastructure is so you can easily understand what’s impacted before you decide to make a change. For instance, if a component within a system is compromised, then you can quickly see and correct what’s been impacted. On the other hand, if you don’t have real-time visibility, then it’s difficult to manage—and you certainly can’t control anything—including costs…
Challenge: This customer relied on their ‘top-shelf’ data center staff to manage each facility separately. As their business grew, the number of data centers grew, and their services required a more sophisticated approach to managing their operations. Faced with managing over a dozen facilities, they realized they needed to mange their operations—all of their data centers—as an integrated system of networks so they could better utilize their resources and manage cost. They also needed a way to quickly and easily report key efficiency and performance metrics to their customers and executive leadership team.
Approach: One component of their strategy was to implement a DCIM system as a global visualization tool. They elected to roll-out their DCIM system capabilities in phases, beginning with gaining visibility of all of their building management systems.
Critical to success: They required built-in colo client-management software and they had a host of metrics they needed to report, such real-time PUE.
Results: Today they are monitoring operations of all equipment. They can detect as early as possible when performance is not up to spec. Decide how and when failures might occur. And use proactive and predictive maintenance. The built-in reports make it much easier to provide their customers with the information and transparency they need to manage their operations.

## Slide 27: Example #2: Capacity
Challenge
    Using Visio and Excel
    Facility data not readily available to IT team for asset mgmt
    Losing site of implementing strategic data center services
Approach
    Streamline IT ops using a single, self-maintainable tool
  Critical to Success
    Integration of existing monitoring systems with other IT mgmt tools, e.g., ticketing systems
    Facility mgmt must embrace the tool
  Results
    Interactive, real-time tool
    Balance of resource management between strategic improvements and efficiency tactics with both IT and Facilities
Notes: Example #2 addresses capacity. It’s based on the experiences a very large enterprise in the Banking & Finance industry.
Challenge: This customer had been managing their IT operations with standard desktop productivity tools, such as Visio and Excel spreadsheets. These tools prevented their team from attaining real-time information because the data had to be imported into spreadsheets, or documents had to be manually updated and archived on a collaboration site. Plus, information sharing was more reactive than proactive. That is, if an IT operations manager wanted to see power and cooling information, then he would need to ask for it.
Consequently, their capacity forecasting relied on wide margins of error. That worked for a while—until their business experienced market pressures that invited scrutiny of their operational effectiveness and web service capabilities. They needed to modernize their data center and their operations to keep up with changing business demands.
Approach: One component of their new data center strategy was to streamline their operations using one tool—a single operational environment—that provided real-time power and cooling information for IT asset management. Plus, it was very important to this customer to ensure both their CMDB data and ticketing system were integrated into their workflow using this tool. Furthermore, they desired a system they could maintain themselves—just like they had been doing with their spreadsheets.
Critical to success: Their data must be transferred to the asset planning environment, and transformed if required. Integration included:
Server power and temperature data
IT asset tracking data
Third-party BMS, PMS and EMS system data
And a key threshold: Their colleagues on the facility operations team must also embrace the tool…
Results:
They are able to integrate their existing monitoring solutions (e.g., BMS, PMS, EMS) with other IT management tools, such as ticketing systems and service management tools through their DCIM system.
They now have a real-time, interactive tool to proactively provide oversight of their data center operations. As a result, they have more complete information that allows them to focus on advancing service delivery rather than chasing the information to resolve maintenance issues.

## Slide 28: Example #3: Control
Notes: Example #3 addresses controls. It’s based on a current project with a large technology enterprise.
In this example we introduce to data centers what has been used in other industrial facilities for decades: Controls. Automation.
Challenge: This customer has an impressive data center operations—very mature with respect to their web services delivery and how they support their business goals. Their limitation had been that they focused strictly on what was going on inside the walled garden of their data centers. At the time, they were well-versed in disaster recovery, but only theoretically. They were aware that their disaster recovery plan wasn’t up to the same technological standards as the rest of their operations. After hearing about the many experiences from ‘Super Storm Sandy’, they decided they couldn’t afford to rely on a checklist of emergency procedures and simply hope for the best. Instead, they took a hard and close look at their ride-through time, as well as their compute workloads, and decided the most practical way to protect their business data and web services was to automate their emergency procedures. (The time between a failure of the data center cooing system and the IT equipment reaching critical temperatures is called the ride-through time and is typically in the range of two minutes or less.)
Approach: Their approach was to design and install a comprehensive DCIM system with automation capabilities. By ‘automate’ we mean both workflow processes and physical infrastructure processes.
Critical to success:
Fully redundant DICM system, i.e., redundancy with the controls and with the application itself
Integration of weather station data into their emergency operation procedures
Instrumenting their data center with flow meters and gas analyzers, also integrated with their DCIM system.
Results: Similar to Examples 1 & 2, they will have a real-time, interactive tool to proactively provide oversight of their data center operations. Moreover, they will have the tools to begin building state-of-the-art, technology-driven methods of procedures for emergencies and disaster recovery.

## Slide 29: In summary…
Visibility
Decision Support
Automation
Notes: That’s a lot to digest… Here’s a summary that’s easier to remember:
A DCIM system provides the visibility, decision support, and automation to effectively manage a flexible network of power, cooling and IT systems.
A DCIM system is the platform for services that provide insight into factors outside of the physical layer, such as highly virtualized environments and the economics and latency of data services.
The use of a DCIM system is expanding in data centers from design through sustained operations—not just for ongoing improvements to efficiency and reliability, but also for deeper integration, including integrating with new technologies, without which we can’t continue to evolve.

## Slide 30: Conclusion
Part 1 – Highlights of TGG white paper #52: Best practices for better data collection, integration and change management
Integrated approach to managing change
Operational documentation
Sequence of operations
Part 2 – The expanding role of DCIM, from design to sustained operations
Latest DCIM definition and models
How DCIM helps with integrating data center operations
Examples using DCIM for managing cost, capacity and control
Notes: Thank you for your attention.

## Slide 31
Questions?

## Slide 32: The Green Grid (TGG)